## 1_Bus_Data
IEEE 33-Bus System — BUS DATA (PSS/E v33 format)
Source: Baran & Wu (1989), IEEE Trans. Power Delivery 4(2) ¦ Base MVA = 100 ¦ Frequency = 50 Hz
Bus No. | Bus Name | Base kV | Type | Area | Zone | Vm (pu) | Va (deg) | Notes
|  |  | 3=Slack 1=Load |  |  | Init=1.0 | Init=0.0
1 | BUS1 | 12.66 | 3 | 1 | 1 | 1 | 0 | SLACK BUS — Grid connection point
2 | BUS2 | 12.66 | 1 | 1 | 1 | 1 | 0
3 | BUS3 | 12.66 | 1 | 1 | 1 | 1 | 0
4 | BUS4 | 12.66 | 1 | 1 | 1 | 1 | 0
5 | BUS5 | 12.66 | 1 | 1 | 1 | 1 | 0
6 | BUS6 | 12.66 | 1 | 1 | 1 | 1 | 0 | Lateral branch point (Bus 26)
7 | BUS7 | 12.66 | 1 | 1 | 1 | 1 | 0
8 | BUS8 | 12.66 | 1 | 1 | 1 | 1 | 0
9 | BUS9 | 12.66 | 1 | 1 | 1 | 1 | 0
10 | BUS10 | 12.66 | 1 | 1 | 1 | 1 | 0
11 | BUS11 | 12.66 | 1 | 1 | 1 | 1 | 0
12 | BUS12 | 12.66 | 1 | 1 | 1 | 1 | 0
13 | BUS13 | 12.66 | 1 | 1 | 1 | 1 | 0
14 | BUS14 | 12.66 | 1 | 1 | 1 | 1 | 0 | Weakest bus — PV placement point
15 | BUS15 | 12.66 | 1 | 1 | 1 | 1 | 0
16 | BUS16 | 12.66 | 1 | 1 | 1 | 1 | 0
17 | BUS17 | 12.66 | 1 | 1 | 1 | 1 | 0
18 | BUS18 | 12.66 | 1 | 1 | 1 | 1 | 0 | End of main feeder
19 | BUS19 | 12.66 | 1 | 1 | 1 | 1 | 0 | Lateral from Bus 2
20 | BUS20 | 12.66 | 1 | 1 | 1 | 1 | 0
21 | BUS21 | 12.66 | 1 | 1 | 1 | 1 | 0
22 | BUS22 | 12.66 | 1 | 1 | 1 | 1 | 0 | End of lateral 1
23 | BUS23 | 12.66 | 1 | 1 | 1 | 1 | 0 | Lateral from Bus 3
24 | BUS24 | 12.66 | 1 | 1 | 1 | 1 | 0 | Heavy load bus
25 | BUS25 | 12.66 | 1 | 1 | 1 | 1 | 0 | Heavy load — end of lateral 2
26 | BUS26 | 12.66 | 1 | 1 | 1 | 1 | 0 | Lateral from Bus 6
27 | BUS27 | 12.66 | 1 | 1 | 1 | 1 | 0 | EV charging placement bus
28 | BUS28 | 12.66 | 1 | 1 | 1 | 1 | 0
29 | BUS29 | 12.66 | 1 | 1 | 1 | 1 | 0
30 | BUS30 | 12.66 | 1 | 1 | 1 | 1 | 0 | High reactive load
31 | BUS31 | 12.66 | 1 | 1 | 1 | 1 | 0 | 2nd weakest — BESS placement
32 | BUS32 | 12.66 | 1 | 1 | 1 | 1 | 0
33 | BUS33 | 12.66 | 1 | 1 | 1 | 1 | 0 | End of lateral 3

## 2_Load_Data
IEEE 33-Bus System — LOAD DATA
Units: MW and MVAr (not per unit) ¦ Bus 1 = Slack, no load ¦ Load ID = '1' for all
Bus No. | Load ID | Status | P Load (MW) | Q Load (MVAr) | IP | IQ | Notes
|  | 1=In service |  |  | 0 | 0
2 | 1 | 1 | 0.1 | 0.06 | 0 | 0
3 | 1 | 1 | 0.09 | 0.04 | 0 | 0
4 | 1 | 1 | 0.12 | 0.08 | 0 | 0
5 | 1 | 1 | 0.06 | 0.03 | 0 | 0
6 | 1 | 1 | 0.06 | 0.02 | 0 | 0
7 | 1 | 1 | 0.2 | 0.1 | 0 | 0
8 | 1 | 1 | 0.2 | 0.1 | 0 | 0
9 | 1 | 1 | 0.06 | 0.02 | 0 | 0
10 | 1 | 1 | 0.06 | 0.02 | 0 | 0
11 | 1 | 1 | 0.045 | 0.03 | 0 | 0
12 | 1 | 1 | 0.06 | 0.035 | 0 | 0
13 | 1 | 1 | 0.06 | 0.035 | 0 | 0
14 | 1 | 1 | 0.12 | 0.08 | 0 | 0
15 | 1 | 1 | 0.06 | 0.01 | 0 | 0
16 | 1 | 1 | 0.06 | 0.02 | 0 | 0
17 | 1 | 1 | 0.06 | 0.02 | 0 | 0
18 | 1 | 1 | 0.09 | 0.04 | 0 | 0
19 | 1 | 1 | 0.09 | 0.04 | 0 | 0
20 | 1 | 1 | 0.09 | 0.04 | 0 | 0
21 | 1 | 1 | 0.09 | 0.04 | 0 | 0
22 | 1 | 1 | 0.09 | 0.04 | 0 | 0
23 | 1 | 1 | 0.09 | 0.05 | 0 | 0
24 | 1 | 1 | 0.42 | 0.2 | 0 | 0 | Heavy load bus
25 | 1 | 1 | 0.42 | 0.2 | 0 | 0 | Heavy load bus
26 | 1 | 1 | 0.06 | 0.025 | 0 | 0
27 | 1 | 1 | 0.06 | 0.025 | 0 | 0
28 | 1 | 1 | 0.06 | 0.02 | 0 | 0
29 | 1 | 1 | 0.12 | 0.07 | 0 | 0
30 | 1 | 1 | 0.2 | 0.6 | 0 | 0 | High Q load — pf = 0.32
31 | 1 | 1 | 0.15 | 0.07 | 0 | 0
32 | 1 | 1 | 0.21 | 0.1 | 0 | 0
33 | 1 | 1 | 0.06 | 0.04 | 0 | 0
TOTAL |  |  | 3.715 | 2.3

## 3_Branch_Data
IEEE 33-Bus System — BRANCH DATA
Base impedance = 12.66^2 / 100 = 1.6028 ohms ¦ R_pu = R_ohm / 1.6028 ¦ B (line charging) = 0 for distribution network
From Bus | To Bus | 1 | 1 | X (ohm) | R (pu) | X (pu) | B (pu) | Rate A (MVA) | Status | Notes
|  | 1 | 1 |  |  |  | 0 | 250 | 1=In svc
1 | 2 | 1 | 1 | 0.047 | 0.057526 | 0.029324 | 0 | 250 | 1 | Main feeder
2 | 3 | 1 | 1 | 0.2511 | 0.3076 | 0.15667 | 0 | 250 | 1
3 | 4 | 1 | 1 | 0.1864 | 0.22836 | 0.1163 | 0 | 250 | 1
4 | 5 | 1 | 1 | 0.1941 | 0.23778 | 0.1211 | 0 | 250 | 1
5 | 6 | 1 | 1 | 0.707 | 0.51099 | 0.44111 | 0 | 250 | 1
6 | 7 | 1 | 1 | 0.6188 | 0.1168 | 0.38609 | 0 | 250 | 1
7 | 8 | 1 | 1 | 0.2351 | 0.44386 | 0.14669 | 0 | 250 | 1
8 | 9 | 1 | 1 | 0.74 | 0.64264 | 0.4617 | 0 | 250 | 1 | Long high-impedance section
9 | 10 | 1 | 1 | 0.74 | 0.65138 | 0.4617 | 0 | 250 | 1 | Long high-impedance section
10 | 11 | 1 | 1 | 0.065 | 0.12266 | 0.040555 | 0 | 250 | 1
11 | 12 | 1 | 1 | 0.1238 | 0.2336 | 0.077242 | 0 | 250 | 1
12 | 13 | 1 | 1 | 1.155 | 0.91592 | 0.72063 | 0 | 250 | 1 | Highest R segment
13 | 14 | 1 | 1 | 0.7129 | 0.33792 | 0.4448 | 0 | 250 | 1
14 | 15 | 1 | 1 | 0.526 | 0.36874 | 0.32819 | 0 | 250 | 1
15 | 16 | 1 | 1 | 0.545 | 0.46564 | 0.34004 | 0 | 250 | 1
16 | 17 | 1 | 1 | 1.721 | 0.80424 | 1.0738 | 0 | 250 | 1 | High X segment
17 | 18 | 1 | 1 | 0.574 | 0.45671 | 0.35813 | 0 | 250 | 1 | End of main feeder
2 | 19 | 1 | 1 | 0.1565 | 0.10232 | 0.097644 | 0 | 250 | 1 | Lateral 1 start — from Bus 2
19 | 20 | 1 | 1 | 1.3554 | 0.93851 | 0.84567 | 0 | 250 | 1 | Highest R in lateral 1
20 | 21 | 1 | 1 | 0.4784 | 0.2555 | 0.29849 | 0 | 250 | 1
21 | 22 | 1 | 1 | 0.9373 | 0.4423 | 0.58481 | 0 | 250 | 1 | End of lateral 1
3 | 23 | 1 | 1 | 0.3083 | 0.28152 | 0.19236 | 0 | 250 | 1 | Lateral 2 start — from Bus 3
23 | 24 | 1 | 1 | 0.7091 | 0.56029 | 0.44243 | 0 | 250 | 1
24 | 25 | 1 | 1 | 0.7011 | 0.55904 | 0.43743 | 0 | 250 | 1 | End of lateral 2
6 | 26 | 1 | 1 | 0.1034 | 0.12666 | 0.064514 | 0 | 250 | 1 | Lateral 3 start — from Bus 6
26 | 27 | 1 | 1 | 0.1447 | 0.17732 | 0.090282 | 0 | 250 | 1
27 | 28 | 1 | 1 | 0.9337 | 0.66074 | 0.58256 | 0 | 250 | 1
28 | 29 | 1 | 1 | 0.7006 | 0.50176 | 0.43712 | 0 | 250 | 1
29 | 30 | 1 | 1 | 0.2585 | 0.31664 | 0.16129 | 0 | 250 | 1
30 | 31 | 1 | 1 | 0.963 | 0.60795 | 0.60084 | 0 | 250 | 1
31 | 32 | 1 | 0.3105 | 0.3619 | 0.19373 | 0.2258 | 0 | 250 | 1
32 | 33 | 1 | 0.341 | 0.5302 | 0.21276 | 0.33081 | 0 | 250 | 1 | End of lateral 3

## 4_Generator_Data
IEEE 33-Bus System — GENERATOR DATA
Only one generator at Bus 1 (slack bus). PSS/E will solve for P and Q to balance the system.
Bus No. | Gen ID | PG (MW) | QG (MVAr) | Qmax (MVAr) | Qmin (MVAr) | Vm (pu) | Status
1 | 1 | 0 | 0 | 9999 | -9999 | 1 | 1
NOTE: PG and QG = 0.0 as initial values only. PSS/E solves these during load flow.

## 5_PSSE_Entry_Guide
PSS/E v33 Data Entry Guide — IEEE 33-Bus System
STEP | ACTION IN PSS/E | NOTES
1 | File -> New Case | Set Base MVA = 100, Frequency = 50 Hz
2 | Network -> Buses -> Add rows from Sheet 1_Bus_Data | Enter all 33 buses. Bus 1 Type=3 (slack), rest Type=1
3 | Network -> Loads -> Add rows from Sheet 2_Load_Data | No load at Bus 1. Load ID = '1' for all
4 | Network -> Branches -> Add rows from Sheet 3_Branch_Data | Use R(pu) and X(pu) columns. B=0, Rate=250 MVA
5 | Network -> Machines -> Add row from Sheet 4_Generator_Data | Slack generator at Bus 1 only
6 | Power Flow -> Solution -> Newton Raphson Load Flow | Keep default settings and click Solve
7 | Power Flow -> Reports -> Bus Voltage and Angle Report | Record Vm(pu) for all 33 buses
8 | Power Flow -> Reports -> System Summation Report | Record total MW losses
9 | File -> Save Case As -> IEEE33bus.sav | Save for future use
10 | Compare results with pandapower column in Sheet 6 | Fill in PSS/E column after solving

## 6_Comparison_Table
Bus Voltage Comparison — pandapower vs PSS/E v33
Fill PSS/E column after running load flow in PSS/E. Difference should be < 0.0005 pu for all buses.
Bus No. | pandapower (pu) | PSS/E v33 (pu) | Difference (pu)
1 | 1 | ← Enter here
2 | 0.997 | ← Enter here
3 | 0.9829 | ← Enter here
4 | 0.9755 | ← Enter here
5 | 0.9681 | ← Enter here
6 | 0.9497 | ← Enter here
7 | 0.9462 | ← Enter here
8 | 0.9413 | ← Enter here
9 | 0.9351 | ← Enter here
10 | 0.9292 | ← Enter here
11 | 0.9284 | ← Enter here
12 | 0.927 | ← Enter here
13 | 0.9208 | ← Enter here
14 | 0.9185 | ← Enter here
15 | 0.9171 | ← Enter here
16 | 0.9132 | ← Enter here
17 | 0.9131 | ← Enter here
18 | 0.9965 | ← Enter here
19 | 0.9929 | ← Enter here
20 | 0.9922 | ← Enter here
21 | 0.9916 | ← Enter here
22 | 0.9827 | ← Enter here
23 | 0.9794 | ← Enter here
24 | 0.9727 | ← Enter here
25 | 0.9694 | ← Enter here
26 | 0.9477 | ← Enter here
27 | 0.9449 | ← Enter here
28 | 0.9337 | ← Enter here
29 | 0.9255 | ← Enter here
30 | 0.922 | ← Enter here
31 | 0.9178 | ← Enter here
32 | 0.9168 | ← Enter here
33 |  | ← Enter here